## Table 1 Simple TCO model
Table 1: Simple model of true cost of ownership for a new high density data center | [7 empty] | Input cells are green. Note, some inputs are below the table and footnotes.
Energy and power use/costs | Units | Servers | Disk storage | Tape storage | Networking | Totals | Notes
% of racks |  | 80% | 8% | 2% | 10% | 100% | 1 | Calculate Watts/thousand $ based on IBM x3550 characteristics
# of racks |  | 160 | 16 | 4 | 20 | 200 | 2 | Street price | 4500
# of U per rack |  | 42 | 42 | 42 | 42 | 42 | 3 | Watts | 385
% filled | % | 76.19% | 76% | 76% | 76% | 76.15% | 4 | Watts/thousand $ | 85.5556
# of U filled |  | 5120 | 510.72 | 127.68 | 638.4 | 6396.8 | 5
potential svgs in watts per server
Power use/filled U | W | 385 | 200 | 50 | 150 | 340.09 | 6 | 0%
Total power use/rack | kW/rack | 12.32 | 6.384 | 1.596 | 4.788 | 10.8774 | 7
Total Direct IT power use | kW | 1971.2 | 102.144 | 6.384 | 95.76 | 2175.488 | 8
Summary of impacts of 20% reduction in server power use
Total electricity use | [7 empty] | 10.5 | million saved in infrastructure costs for 20% server savings
IT (UPS) load | kW | 1971.2 | 102.144 | 6.384 | 95.76 | 2175.488 | 8 | 2050.7812 | $/server saved in infrastructure costs
Cooling | kW | 1281.28 | 66.3936 | 4.1496 | 62.244 | 1414.0672 | 9
Auxiliaries | kW | 689.92 | 35.7504 | 2.2344 | 33.516 | 761.4208 | 10 | 0.45 | M$ saved in electricity costs
Total power use | kW | 3942.4 | 204.288 | 12.768 | 191.52 | 4350.976 | 11 | 87.8906 | $/server saved per year in electricity costs for 20% reduction (including cooling and auxiliaries)
Electric power density | [7 empty] | 6.5 | M kWh/yr saved for 20% reduction in server power
IT load | W/sf elect. Active | 98.56 | 5.1072 | 0.3192 | 4.788 | 108.7744 | 12 | 1269.5312 | kWh/yr per server saved in electricity use (including cooling and auxiliaries)
Cooling | W/sf elect. Active | 64.064 | 3.3197 | 0.20748 | 3.1122 | 70.7034 | 12
Auxiliaries | W/sf elect. Active | 34.496 | 1.7875 | 0.11172 | 1.6758 | 38.071 | 12
Total power use | W/sf elect. Active | 197.12 | 10.2144 | 0.6384 | 9.576 | 217.5488 | 12
Total electricity consumption
IT load | M kWh/year | 16.4156 | 0.85062 | 0.053164 | 0.79746 | 18.1168 | 13
Cooling | M kWh/year | 10.6701 | 0.55291 | 0.034557 | 0.51835 | 11.7759 | 13
Auxiliaries | M kWh/year | 5.7454 | 0.29772 | 0.018607 | 0.27911 | 6.3409 | 13
Total electricity use | M kWh/year | 32.8311 | 1.7012 | 0.10633 | 1.5949 | 36.2336 | 13
Total energy cost
IT load | M $/year | 1.1145 | 0.057754 | 0.0036096 | 0.054144 | 1.23 | 14
Cooling | M $/year | 0.72445 | 0.03754 | 0.0023462 | 0.035194 | 0.79953 | 14
Auxiliaries | M $/year | 0.39009 | 0.020214 | 0.0012634 | 0.01895 | 0.43052 | 14
Total electricity cost | M $/year | 2.2291 | 0.11551 | 0.0072192 | 0.10829 | 2.4601 | 14
Capital costs (Cap Ex)
IT capital costs
Watts per thousand $ of IT costs | watts/thousand $ | 85.5556 | 30 | 6 | 100 |  | 15
Cost per filled U | k $/U | 4.5 | 6.6667 | 8.3333 | 1.5 |  | 16
Cost per filled rack | k $/rack | 189 | 280 | 350 | 63 |  | 17
Total IT costs | M $ | 23.04 | 3.4048 | 1.064 | 0.9576 | 28.4664 | 18
Other capital costs | Units | Servers | Disk storage | Tape storage | Networking | Totals | Notes
Rack costs | k $/rack | 3 | 3 | 3 | 3 |  | 19
External hardwired connections | k $/rack | 5 | 5 | 5 | 5 |  | 20
Internal routers and switches | k $/rack | 5 | 5 | 5 | 5 |  | 21
Rack management hardware | k $/rack | 3 | 3 | 3 | 3 |  | 22
Rack costs total | M $ | 0.48 | 0.048 | 0.012 | 0.06 | 0.6 | 23
External hardwired connections total | M $ | 0.8 | 0.08 | 0.02 | 0.1 | 1 | 23
Internal routers and switches total | M $ | 0.8 | 0.08 | 0.02 | 0.1 | 1 | 23
Rack management hardware total | M $ | 0.48 | 0.048 | 0.012 | 0.06 | 0.6 | 23
Cabling costs (total) | [5 empty] | 1.3 | 24
Point of Presence (POP) | M $ |  |  |  |  | 3.5 | 25
kW related infrastructure costs | M $ | 46.9166 | 2.4311 | 0.15195 | 2.2792 | 51.7789 | 26
Other facility costs (elect. active) | M $ |  |  |  |  | 5.2362 | 27
Interest during construction | M $ |  |  |  |  | 3.9911 | 28
Land costs | M $ |  |  |  |  | 0.5 | 29
Architectural and engineering fees | M $ |  |  |  |  | 2.8508 | 30
Inert gas fire suppression | M $ |  |  |  |  | 1 | 31
[9 empty] | based on |  | Based on
Total installed capital costs | M $ |  |  |  |  | 101.8234 |  |  | cap. Costs |  | annualized capital costs
| $/sf elect. active |  |  |  |  | 5091.1686 |  |  | % | M$ | %
Capital costs with 3 year life | M $ |  |  |  |  | 30.0664 | 32 | IT costs | 29.53% | 11.4569 | 59.25% | Note: in the first version of the model there was an error
Capital costs with 15 year life | M $ |  |  |  |  | 71.757 | 33 | Infrastructure | 70.47% | 7.8785 | 40.75% | in cells L72 and L73. The IT costs and infrastructure costs
[10 empty] | 19.3354 | 100% | cells were switched. That error has been corrected here and
Annualized capital costs | M $/year |  |  |  |  | 19.3354 | 34 |  |  |  |  | in the graph (Jonathan Koomey, 18 Oct 07, JGKoomey@stanford.edu)
Annual operating expenses (Op Ex)
[9 empty] | Annualized costs | %
Total electricity costs | M $/year | 2.2291 | 0.11551 | 0.0072192 | 0.10829 | 2.4601 | 35 | Energy costs | 2.4601 | 9.762%
Network fees | M $/year |  |  |  |  | 0.5 | 36 | Other operating expenses | 3.4056 | 13.51%
Other operating expenses | [6 empty] | 37 | Site infrastructure capital costs | 7.8785 | 31.26%
IT site management staff | M $/year |  |  |  |  | 0.39 | 38 | IT capital costs | 11.4569 | 45.46%
Facilities site management staff | M $/year |  |  |  |  | 0.52 | 39
Maintenance | M $/year |  |  |  |  | 0.416 | 40 |  | 25.201 | 100%
Janitorial and landscaping | M $/year |  |  |  |  | 0.16 | 41
Security | M $/year |  |  |  |  | 0.702 | 42
Property taxes | M $/year |  |  |  |  | 0.71757 | 43 | Infrastructure related costs
Total other operating expenses | M $/year |  |  |  |  | 2.9056 |  | Capital | 7.8785 | 31.26%
[8 empty] | Energy costs | 1.23 | 4.881%
Total operating expenses | M $/year |  |  |  |  | 5.8657 | 44 | Other operating expenses | 2.5156 | 9.982%
[9 empty] | 11.6241 | 46.13%
Total Annualized costs | [7 empty] | IT related costs
Total | M $/year |  |  |  |  | 25.201 | 45 | Capital | 11.4569 | 45.46%
Per unit of electrically active floor space | $/sf/year |  |  |  |  | 1260.0524 | 46 | Energy costs | 1.23 | 4.881%
Per server | $/server/year |  |  |  |  | 4922.0799 | 47 | Other operating expenses | 0.89 | 3.532%
Assumptions (Note: All costs are 2007 dollars. Contact JGKoomey@stanford.edu with questions or comments) | [8 empty] | 13.5769 | 53.87%
1) Fraction of racks allocated to different categories based on Uptime institute consulting experience and judgment for high performance computing in financial applications. | [7 empty] | Total | 25.201 | 100%
2) Number of racks calculated based on 20ksf electrically active floor area, 100 square feet per rack, and percentage breakdown from previous row.
3) Racks are standard (6.5 feet high with 42 Us per rack).
4) % of rack filled based on Uptime consulting experience.
5) The total number of Us filled is the product of the number of racks times total Us per rack times the % filled.
6) Energy use per U taken from selective review of market/technology data. Server power and costs per watt assumes IBM X-3550 1U system.
7) Energy use per rack is the product of the total number of Us filled times watts per installed U.
8) Total direct IT energy use is the product of watts per rack times the number of racks of a given type.
9) Cooling electricity use (including chillers, fans, pumps, CRAC units) is estimated as 0.65 times the IT load .
10) Auxiliaries electricity use (including UPS/PDU losses, lights, and other losses) is estimated as 0.35 times IT load.
11) Total electricity use is the sum of IT, cooling, and auxiliaries. Cooling and auxiliaries together are equal to the IT load (Power overhead multiplier = 2.0).
12) Electricity intensity is calculated by dividing the power associated with a particular component (eg IT load) by the total electrically active area of the facility.
13) Total electricity consumption is calculated using the total power, a power load factor of 95%, and 8766 hours/year (average over leap and non-leap years).
14) Total energy cost calculated by multiplying electricity consumption by the average U.S. industrial electricity price in 2007 (6.8 cents/kWh, 2007 dollars).
15) Watts per thousand 2007 dollars of IT costs taken from selective review of market and technology data. Server number calculated assuming IBM x3550 1U server as described in next note.
16) Cost per filled U taken from selective review of market and technology data. Server street cost calculated assuming IBM x3550 1U server with 8 GB RAM, two dual core 2.66 GHz Intel processors (19.2 GFLOPS max/server).
17) Cost per filled rack is the product of the cost per U and the total # of Us per rack (42).
18) Total IT costs are the product of the number of filled Us and the cost per filled U.
19) Rack costs are the costs of the rack structure alone.
20) External hardwired connections costs are Uptime estimates.
21) Internal routers and switch costs are Uptime estimates.
22) Rack management hardware costs are Uptime estimates.
23) Total costs for racks, hardwired connections, and internal routers and switches are the product of the cost per rack and the number of racks.
24) Cabling costs totals are Uptime estimates.
25) Point of presence costs are Uptime estimates for a dual POP OC96 installation.
26) kW related infrastructure costs (taken from Turner and Seader 2006) are based on Tier 3 architecture, $23,801 per kW cost. Assumes immediate full build out. Includes costs for non electrically active area. Construction costs escalated to 2007$ using Turner construction cost indices for 2005 and 2006 (http://www.turnerconstruction.com/corporate/content.asp?d=20) and 2007 forecast (http://www.turnerconstruction.com/corporate/content.asp?d=5952). Electricity prices escalated to 2007$ using the GDP deflator 2005 to 2006 and 3% inflation for 2006 to 2007.
27) Other facility costs are based on $262 per square foot of electrically active area (taken from Turner and Seader 2006. Costs are in 2007 $, escalated as described in the previous footnote).
28) Interest during construction estimated based on total infrastructure and other facility capital costs assuming a 7% real interest rate for one year.
29) Land cost based on $100,000 per acre, 5 acres total.
30) Architectural and engineering fees are estimated as 5% of kW related infrastructure costs plus other facility costs (electrically active). Cost percentage is based on personal communication with Peter Rumsey of Rumsey Engineers, 9 July 2007.
31) Cost for inert gas fire suppression are Uptime estimates ($50/sf of electrically active floor area).
32) Capital costs with three year life include all IT equipment costs (which include internal routers and switches).
33) Capital costs with 15 year lifetime include all capital costs besides IT costs (these costs also include rack, cabling, and external hardwire connection costs).
34) Capital costs are annualized with the capital recovery factor calculated using the appropriate lifetime (three or 15 years) and a 7% real discount rate.
35) Total electricity costs include both IT and infrastructure energy costs (see notes 11, 12, 13, and 14).
36) Network fees are Uptime estimates.
37) Other operating expenses based on Uptime Institute estimates for a Midwest mid-size town location. Benefits are assumed to be equal to 30% of salary.
38) IT site management staff costs assume $100k/yr salary, 3 people per shift, 1 shift per day.
39) Facilities site management staff costs assume $100k/yr salary, 3 people per shift, 1 shift per day.
40) Maintenance costs assume non-union in-house facilities staff, $80k/yr salary, 4 people per shift, 1 shift per day.
41) Janitorial and landscaping costs assume $4/gross square foot of building area per year (based on Uptime estimates).
42) Security costs assume $60k/yr salary, 3 people per shift, 3 shifts per day.
43) Annual property taxes estimated as 1% of the total installed capital cost of the building (not including IT costs).
44) Total operating expenses include electricity costs, network fees, and other operating expenses.
45) Total annualized costs include capital and operating costs.
46) Costs per square foot per year are calculated by dividing total annualized costs by the total electrically active floor area.
47) Costs per server are calculated assuming that all servers are 1U Volume servers and by dividing total annualized costs by the number of Us occupied by servers.
All costs are in year 2007 dollars.
|  |  |  | years | CRF
Total floor area per rack | 100 |  |  | 3 | 0.38105
# of racks in IT space | 200 |  |  | 15 | 0.10979
|  |  |  | 7% | real discount rate
|  | 2005 $/sf | 2007 $/sf
Power related cost | $/kW | 20000 | 23801.06 | Architectural and engineering fees |  | 5% | of building and infrastructure costs
Area-related cost (electrically active) | $/sf | 220 | 261.8117 | Annual property taxes |  | 1% | % of total cost of building (annually), not including IT costs
Inert gas fire suppress costs | 50 | $/sf of electrically active area | [7 empty] | 2005 $/sf | 2007 $/sf
[8 empty] | Power related cost for Tier 4 facilities |  | 22000 | 26181.166
US average industrial price of electricity |  | 0.067895 | $/kWh (year 2007 from AEO 2007, in 2007 $)
Average hours per year (includes leap years) |  | 8766 | hours
Load factor (power, not computation) |  | 95% | accounts for seasonal variation in ambient outside temperature. IT equipment is assumed to be running at full capacity (this is a high density facility for scientific computing applications for finance)
Gross up IT load to get total data center loads: Rules of thumb (typical for full facilities according to Pitt)
IT (UPS load) | 1
Cooling (chillers, fans, pumps) | 0.65 | times UPS load |  |  |  | % of energy use
Auxiliaries (UPS/PDU losses, lighting, other) | 0.35 | times UPS load |  |  |  | IT | 50%
Total | 2 | Site infrastructure overhead multiplier |  |  |  | Infrastructure | 50%
Land | k $/acre | 100 |  |  |  | Total | 100%
Number of acres of land needed | 5
% of floor space for infrastructure
Electrically active floor area | 0%
Additional floor area | 100%
Other facility costs (infrastructure area) | M $
|  | Total | for IT | For infrastructure
Total electrically active floor area | ksf | 20 | 20 | 0
Additional floor area for infrastructure | ksf | 20 | 0 | 20 | Total is for a Tier 3 facility (1 to 1 correspondance between electrically active area and other area. For Tier 4 it is 1 to 1.2).
Total |  | 40 | 20 | 20
|  |  | IT site | Facilities site
|  |  | Mgmt | Mgmt | Maintenance |  | Security
| Salary per person | k$/year | 100 | 100 | 80 |  | 60
| People per shift | # | 3 | 4 | 4 |  | 3
| Shifts per day | # | 1 | 1 | 1 |  | 3
| benefits percentage | % | 30% | 30% | 30% |  | 30%
| Total cost per year | k$/year | 390 | 520 | 416 |  | 702
Janitorial and landscaping costs | 4 | $/gross sf/year | Pitt Turner's estimate.
Security cost often excluded, but should be similar to facility cost (24 hr/day, 1-2 people per shift)--it often appears in another part of the organization's budget.

## Fig 1 Annualized cost %
For the report
For presentations

## Price indices
Price indices
From
Table 1.1.4. Price Indexes for Gross Domestic Product |  |  |  |  | Price indices based on turner construction cost indices, http://www.turnerconstruction.com/corporate/content.asp?d=20
Downloaded 1 Feb 07 from http://bea.gov/bea/dn/nipaweb/SelectTable.asp?Selected=Y
1929 | 11.943 | [5 empty] | Index | Annual growth
1930 | 11.48 |  |  |  |  | 2005 | 717
1931 | 10.334 |  |  |  |  | 2006 | 793 | 10.6%
1932 | 9.15 |  |  |  |  | 2007 | 853.268 | 7.6% | Use 7.6% forecast Q2 2007 rel to Q2 2006, http://www.turnerconstruction.com/corporate/content.asp?d=5952
1933 | 8.91
1934 | 9.351
1935 | 9.534
1936 | 9.644
1937 | 9.998
1938 | 9.81
1939 | 9.688
1940 | 9.771
1941 | 10.405
1942 | 11.255
1943 | 11.885
1944 | 12.165
1945 | 12.478
1946 | 13.934
1947 | 15.488
1948 | 16.372
1949 | 16.364
1950 | 16.493
1951 | 17.626
1952 | 18.009
1953 | 18.24
1954 | 18.434
1955 | 18.709
1956 | 19.36
1957 | 20.039
1958 | 20.512
1959 | 20.754
1960 | 21.044
1961 | 21.281
1962 | 21.572
1963 | 21.801
1964 | 22.134
1965 | 22.538
1966 | 23.18
1967 | 23.897
1968 | 24.916
1969 | 26.153
1970 | 27.538
1971 | 28.916
1972 | 30.171
1973 | 31.854
1974 | 34.721
1975 | 38.007
1976 | 40.202
1977 | 42.758
1978 | 45.762
1979 | 49.553
1980 | 54.062
1981 | 59.128
1982 | 62.738
1983 | 65.214
1984 | 67.664
1985 | 69.724
1986 | 71.269
1987 | 73.204
1988 | 75.706
1989 | 78.569
1990 | 81.614
1991 | 84.457
1992 | 86.402
1993 | 88.39
1994 | 90.265
1995 | 92.115
1996 | 93.859
1997 | 95.415
1998 | 96.475
1999 | 97.868
2000 | 100
2001 | 102.402
2002 | 104.193
2003 | 106.409
2004 | 109.429
2005 | 112.744
2006 | 116.053
2007 | 119.5346 | assume | 3% | growth in prices 2006 to 2007

## aeo2007
Report #: DOE/EIA-0383(2007)
Release date full report: February 2007
Next release date full report: February 2008
Table 3. Energy Prices by Sector and Source
(2005 dollars per million Btu, unless otherwise noted)
2005-
| 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2030
Residential
Liquefied Petroleum Gases | 18.2104 | 19.2934 | 21.1584 | 24.5404 | 24.4948 | 23.96 | 23.6724 | 23.2634 | 23.1067 | 22.9057 | 22.943 | 22.8816 | 22.9797 | 23.1905 | 23.1291 | 23.0885 | 23.1834 | 23.1547 | 23.2855 | 23.4205 | 23.5405 | 23.5322 | 23.5625 | 23.6532 | 23.782 | 23.869 | 23.9091 | 0.8617%
Distillate Fuel Oil | 12.8933 | 14.7271 | 16.9067 | 17.4485 | 16.9105 | 15.8368 | 14.8749 | 14.0318 | 13.3595 | 12.5964 | 12.5241 | 12.5955 | 12.6309 | 12.7381 | 12.8304 | 13.0523 | 13.1472 | 13.2631 | 13.4222 | 13.3606 | 13.5138 | 13.5604 | 13.6274 | 13.8018 | 13.8979 | 14.0583 | 14.1256 | -0.1667%
Natural Gas | 10.7212 | 12.4282 | 13.0407 | 11.8342 | 11.741 | 11.2508 | 10.976 | 10.5919 | 10.4412 | 10.2498 | 10.2927 | 10.2422 | 10.3305 | 10.5577 | 10.4871 | 10.4393 | 10.54 | 10.5361 | 10.6744 | 10.8301 | 10.9481 | 10.9736 | 11.0175 | 11.1168 | 11.2574 | 11.3709 | 11.4261 | -0.3357%
Electricity | 27.099 | 27.5879 | 27.6366 | 27.492 | 27.3681 | 27.1549 | 26.9128 | 26.5094 | 26.2812 | 26.1725 | 26.0365 | 25.9936 | 26.0853 | 26.3049 | 26.445 | 26.3556 | 26.3687 | 26.4193 | 26.421 | 26.4647 | 26.5621 | 26.6082 | 26.5649 | 26.5695 | 26.6057 | 26.7373 | 26.758 | -0.1221%
Commercial
Distillate Fuel Oil | 10.4803 | 12.6794 | 14.6322 | 15.3236 | 14.4385 | 13.4501 | 12.7189 | 11.981 | 11.3383 | 10.846 | 10.6675 | 10.728 | 10.8702 | 10.9252 | 11.0219 | 11.2923 | 11.3498 | 11.461 | 11.6883 | 11.5127 | 11.6838 | 11.8503 | 11.8575 | 12.0538 | 12.253 | 12.3259 | 12.453 | -0.07204%
Residual Fuel Oil | 6.249 | 8.4144 | 10.1003 | 7.8816 | 7.7979 | 7.6791 | 7.5375 | 7.0601 | 6.9191 | 5.9907 | 6.3125 | 6.4942 | 6.4476 | 6.5857 | 6.7015 | 6.989 | 7.0691 | 7.2426 | 7.4012 | 7.2363 | 7.3776 | 7.1704 | 7.2998 | 7.3952 | 7.4625 | 7.2387 | 7.3114 | -0.5605%
Natural Gas | 9.4025 | 11.2028 | 11.3787 | 10.2689 | 10.1576 | 9.6297 | 9.3357 | 8.9214 | 8.7509 | 8.5352 | 8.5525 | 8.4769 | 8.546 | 8.7392 | 8.6564 | 8.5964 | 8.6743 | 8.6351 | 8.7471 | 8.8686 | 8.9717 | 8.9598 | 8.9778 | 9.0513 | 9.1703 | 9.2455 | 9.3029 | -0.7406%
Electricity | 24.5915 | 25.2518 | 25.7384 | 25.3377 | 25.2685 | 24.9183 | 24.5005 | 23.8595 | 23.5936 | 23.4435 | 23.3118 | 23.3281 | 23.4844 | 23.7498 | 23.9443 | 23.8893 | 23.9523 | 24.0005 | 24.0064 | 24.0778 | 24.1956 | 24.231 | 24.1812 | 24.1571 | 24.2073 | 24.2877 | 24.2672 | -0.159%
Industrial 1/
Liquefied Petroleum Gases | 11.1755 | 16.96 | 18.9579 | 17.5131 | 17.3894 | 16.7502 | 16.4239 | 15.9433 | 15.7694 | 15.621 | 15.6275 | 15.5655 | 15.6823 | 15.8656 | 15.8663 | 15.8648 | 15.9074 | 15.8831 | 15.9945 | 16.1068 | 16.2547 | 16.2193 | 16.2301 | 16.319 | 16.4173 | 16.5085 | 16.5492 | -0.09802%
Distillate Fuel Oil | 10.9899 | 13.0815 | 15.1407 | 15.4356 | 14.292 | 13.4233 | 12.9481 | 12.478 | 11.8828 | 11.6418 | 11.3491 | 11.4019 | 11.6325 | 11.6325 | 11.7377 | 12.0607 | 12.0406 | 12.1396 | 12.4212 | 12.1694 | 12.3622 | 12.6196 | 12.5787 | 12.7881 | 13.0696 | 13.0597 | 13.2463 | 0.05012%
Residual Fuel Oil | 5.7739 | 7.7708 | 9.3422 | 9.8767 | 10.0842 | 9.7907 | 9.5023 | 8.7792 | 8.4677 | 8.0373 | 7.9767 | 8.2131 | 8.411 | 8.5568 | 8.6101 | 8.8084 | 8.9135 | 9.0664 | 9.2085 | 9.1495 | 9.2911 | 9.2584 | 9.3849 | 9.5039 | 9.4976 | 9.6069 | 9.5831 | 0.842%
Natural Gas 2/ | 6.4689 | 8.1628 | 7.4494 | 7.3632 | 7.2902 | 6.7422 | 6.4268 | 6.0214 | 5.8671 | 5.6813 | 5.69 | 5.6505 | 5.7415 | 5.9198 | 5.8755 | 5.836 | 5.9 | 5.8859 | 6.0041 | 6.1238 | 6.2413 | 6.2103 | 6.2539 | 6.333 | 6.4338 | 6.5134 | 6.5599 | -0.8706%
Metallurgical Coal | 2.3078 | 3.06 | 3.2548 | 3.2975 | 3.2873 | 3.1889 | 3.0941 | 2.9915 | 2.8927 | 2.7893 | 2.7409 | 2.7166 | 2.7061 | 2.7064 | 2.7045 | 2.6898 | 2.7073 | 2.7181 | 2.7191 | 2.7064 | 2.6859 | 2.6957 | 2.705 | 2.7168 | 2.7307 | 2.7413 | 2.7547 | -0.4196%
Other Industrial Coal | 1.803 | 2.15 | 2.2006 | 2.2393 | 2.2451 | 2.2358 | 2.2615 | 2.2481 | 2.2309 | 2.2124 | 2.2059 | 2.1968 | 2.1891 | 2.1857 | 2.1763 | 2.1755 | 2.1818 | 2.1954 | 2.2051 | 2.209 | 2.2188 | 2.2309 | 2.2424 | 2.2517 | 2.2682 | 2.2746 | 2.2863 | 0.2461%
Coal to Liquids | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.88957 | 0.88125 | 0.88442 | 0.89085 | 0.88841 | 0.89323 | 0.90441 | 0.91453 | 0.9547 | 0.96978 | 1.0133 | 1.0278 | 1.0294 | 1.122 | 1.2297 | 1.2694 | 1.2834 | 1.3287 | 1.3301 | 1.3345 | N/A
Electricity | 15.8848 | 16.6911 | 18.2582 | 18.7686 | 18.8538 | 18.5182 | 18.014 | 17.2543 | 16.7903 | 16.5901 | 16.4669 | 16.4616 | 16.6056 | 16.8515 | 17.0212 | 17.0009 | 17.0709 | 17.1261 | 17.1409 | 17.2065 | 17.3263 | 17.3538 | 17.3105 | 17.3004 | 17.3316 | 17.4254 | 17.4307 | 0.1736%
Transportation
Liquefied Petroleum Gases 3/ | 19.6766 | 23.9161 | 26.8056 | 22.711 | 22.7591 | 22.2688 | 24.3438 | 23.9325 | 23.7633 | 23.5364 | 23.5619 | 23.4868 | 23.5607 | 23.7542 | 23.6548 | 23.5775 | 23.6644 | 23.6253 | 23.7411 | 23.8701 | 23.9738 | 23.9534 | 23.9759 | 24.0566 | 24.1739 | 24.2587 | 24.289 | 0.06189%
E85 4/ | 20.9149 | 23.1019 | 24.8115 | 27.7748 | 25.9953 | 24.2666 | 21.2913 | 20.5252 | 20.3361 | 20.1974 | 20.0099 | 20.0933 | 20.1963 | 20.4328 | 20.4077 | 20.6243 | 20.6104 | 20.6177 | 21.0671 | 20.9702 | 20.9622 | 21.2579 | 21.0981 | 21.3195 | 21.4387 | 21.3984 | 21.4992 | -0.2872%
Motor Gasoline 5/ | 15.7218 | 18.6449 | 21.1535 | 20.9645 | 19.721 | 18.6921 | 17.9023 | 17.2322 | 16.8638 | 16.5659 | 16.0857 | 16.0633 | 16.112 | 16.2404 | 16.3247 | 16.6729 | 16.632 | 16.7513 | 17.0515 | 16.9203 | 17.1026 | 17.3232 | 17.1443 | 17.2929 | 17.5313 | 17.5268 | 17.7561 | -0.1952%
Jet Fuel 6/ | 9.2184 | 13.1439 | 14.9574 | 12.9907 | 11.7224 | 11.2625 | 10.9057 | 10.3721 | 10.0592 | 10.0335 | 9.8431 | 9.8874 | 10.0323 | 10.0872 | 10.2108 | 10.5231 | 10.5069 | 10.588 | 10.8931 | 10.7885 | 10.9106 | 11.0979 | 11.0487 | 11.2275 | 11.5179 | 11.509 | 11.7494 | -0.4476%
Distillate Fuel Oil 7/ | 13.5833 | 17.5225 | 19.7922 | 19.7063 | 18.2112 | 17.3086 | 16.8089 | 16.0012 | 15.3922 | 15.213 | 14.8221 | 14.8599 | 15.1214 | 15.0758 | 15.1581 | 15.4796 | 15.4157 | 15.4886 | 15.7731 | 15.4717 | 15.6397 | 15.9126 | 15.834 | 16.0258 | 16.3338 | 16.2625 | 16.471 | -0.2472%
Residual Fuel Oil | 4.8536 | 5.5068 | 7.1623 | 8.8221 | 9.0483 | 8.6029 | 8.0482 | 7.6903 | 7.343 | 7.1018 | 6.9725 | 7.0414 | 7.0324 | 7.1228 | 7.1432 | 7.1685 | 7.359 | 7.4886 | 7.6476 | 7.6767 | 7.8516 | 7.8974 | 8.037 | 8.1833 | 8.1197 | 8.3803 | 8.2735 | 1.642%
Natural Gas 8/ | 11.9137 | 14.7612 | 11.9819 | 12.2833 | 12.1389 | 12.317 | 13.9655 | 13.5076 | 13.2914 | 13.0437 | 12.9408 | 12.8616 | 12.8948 | 13.0292 | 12.949 | 12.9462 | 12.9757 | 12.9531 | 13.0798 | 13.1107 | 13.1985 | 13.2244 | 13.1752 | 13.2406 | 13.36 | 13.3953 | 13.4536 | -0.3703%
Electricity | 26.1036 | 25.2162 | 26.121 | 25.6292 | 25.7473 | 25.3928 | 24.8616 | 24.3179 | 24.1258 | 23.9807 | 23.7874 | 23.8097 | 23.8764 | 24.0748 | 24.2621 | 24.1838 | 24.217 | 24.2459 | 24.2234 | 24.3074 | 24.428 | 24.4657 | 24.3868 | 24.3451 | 24.4017 | 24.4821 | 24.4609 | -0.1216%
Electric Power 9/
Distillate Fuel Oil | 9.5154 | 11.3847 | 13.2358 | 14.2634 | 13.7692 | 12.7042 | 11.7052 | 10.7795 | 10.0299 | 9.2897 | 9.1973 | 9.2599 | 9.2776 | 9.4403 | 9.5352 | 9.7515 | 9.8428 | 9.9595 | 10.1106 | 10.0771 | 10.2175 | 10.2541 | 10.3189 | 10.4858 | 10.5727 | 10.74 | 10.7862 | -0.2158%
Residual Fuel Oil | 4.991 | 6.9611 | 7.8458 | 7.1944 | 7.2948 | 6.9926 | 6.5808 | 6.2065 | 5.9029 | 5.4571 | 5.4534 | 5.5995 | 5.6287 | 5.7371 | 5.8141 | 6.0071 | 6.0822 | 6.2296 | 6.4187 | 6.3188 | 6.5342 | 6.5805 | 6.637 | 6.7344 | 6.7479 | 6.8498 | 6.847 | -0.0661%
Natural Gas | 6.1141 | 8.1813 | 6.9708 | 7.1151 | 7.0668 | 6.5266 | 6.2203 | 5.8298 | 5.6926 | 5.4996 | 5.541 | 5.5007 | 5.5974 | 5.7881 | 5.7226 | 5.6709 | 5.7639 | 5.726 | 5.8378 | 5.9462 | 6.0574 | 6.0477 | 6.0664 | 6.148 | 6.2517 | 6.3135 | 6.3304 | -1.021%
Steam Coal | 1.4012 | 1.53 | 1.6714 | 1.6918 | 1.704 | 1.7 | 1.7052 | 1.6668 | 1.637 | 1.62 | 1.613 | 1.5999 | 1.5919 | 1.5892 | 1.576 | 1.578 | 1.581 | 1.589 | 1.5983 | 1.602 | 1.6149 | 1.6283 | 1.6393 | 1.6501 | 1.6656 | 1.6749 | 1.6897 | 0.398%
Average Price to All Users 10/
Liquefied Petroleum Gases | 12.6907 | 17.4824 | 19.4641 | 18.9956 | 18.8806 | 18.2866 | 18.0201 | 17.5716 | 17.4176 | 17.2679 | 17.2913 | 17.2417 | 17.3648 | 17.5622 | 17.5628 | 17.5588 | 17.6206 | 17.5993 | 17.7214 | 17.8418 | 17.9908 | 17.9618 | 17.9887 | 18.0769 | 18.1849 | 18.2631 | 18.3043 | 0.1839%
E85 4/ | 20.9149 | 23.1019 | 24.8115 | 27.7748 | 25.9953 | 24.2666 | 21.2913 | 20.5252 | 20.3361 | 20.1974 | 20.0099 | 20.0933 | 20.1963 | 20.4328 | 20.4077 | 20.6243 | 20.6104 | 20.6177 | 21.0671 | 20.9702 | 20.9622 | 21.2579 | 21.0981 | 21.3195 | 21.4387 | 21.3984 | 21.4992 | -0.2872%
Motor Gasoline 5/ | 15.706 | 18.6021 | 21.108 | 20.9627 | 19.7201 | 18.6906 | 17.9005 | 17.2304 | 16.8618 | 16.5642 | 16.084 | 16.0616 | 16.1101 | 16.2386 | 16.323 | 16.6711 | 16.6302 | 16.7495 | 17.0497 | 16.9185 | 17.1009 | 17.3214 | 17.1425 | 17.2911 | 17.5295 | 17.5252 | 17.7543 | -0.1864%
Jet Fuel | 9.2184 | 13.1439 | 14.9574 | 12.9907 | 11.7224 | 11.2625 | 10.9057 | 10.3721 | 10.0592 | 10.0335 | 9.8431 | 9.8874 | 10.0323 | 10.0872 | 10.2108 | 10.5231 | 10.5069 | 10.588 | 10.8931 | 10.7885 | 10.9106 | 11.0979 | 11.0487 | 11.2275 | 11.5179 | 11.509 | 11.7494 | -0.4476%
Distillate Fuel Oil | 12.9106 | 16.217 | 18.4216 | 18.4379 | 17.1991 | 16.2963 | 15.7045 | 14.9218 | 14.3602 | 14.183 | 13.8626 | 13.9159 | 14.1535 | 14.1446 | 14.24 | 14.5584 | 14.5279 | 14.619 | 14.9022 | 14.6464 | 14.8252 | 15.0819 | 15.0313 | 15.2354 | 15.5303 | 15.5008 | 15.7047 | -0.1283%
Residual Fuel Oil | 5.0985 | 6.5886 | 7.9185 | 8.253 | 8.405 | 8.0573 | 7.6088 | 7.1944 | 6.8676 | 6.4548 | 6.4073 | 6.547 | 6.5696 | 6.6816 | 6.7372 | 6.8651 | 6.9957 | 7.1397 | 7.3089 | 7.2671 | 7.4511 | 7.4737 | 7.5808 | 7.7013 | 7.6767 | 7.8322 | 7.7872 | 0.6708%
Natural Gas | 7.8259 | 9.6488 | 9.1378 | 8.7612 | 8.6626 | 8.1271 | 7.8336 | 7.4448 | 7.2887 | 7.0927 | 7.115 | 7.0642 | 7.152 | 7.347 | 7.2896 | 7.2449 | 7.3208 | 7.3071 | 7.4372 | 7.57 | 7.6925 | 7.6795 | 7.7305 | 7.8213 | 7.9384 | 8.0274 | 8.0851 | -0.7047%
Metallurgical Coal | 2.3078 | 3.06 | 3.2548 | 3.2975 | 3.2873 | 3.1889 | 3.0941 | 2.9915 | 2.8927 | 2.7893 | 2.7409 | 2.7166 | 2.7061 | 2.7064 | 2.7045 | 2.6898 | 2.7073 | 2.7181 | 2.7191 | 2.7064 | 2.6859 | 2.6957 | 2.705 | 2.7168 | 2.7307 | 2.7413 | 2.7547 | -0.4196%
Other Coal | 1.4307 | 1.5707 | 1.706 | 1.7269 | 1.7392 | 1.7345 | 1.7402 | 1.7027 | 1.6732 | 1.6556 | 1.6479 | 1.6347 | 1.6264 | 1.6231 | 1.6098 | 1.6111 | 1.6137 | 1.6215 | 1.6301 | 1.6332 | 1.6453 | 1.6582 | 1.6687 | 1.6788 | 1.6939 | 1.7025 | 1.7166 | 0.3559%
Coal to Liquids | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.88957 | 0.88125 | 0.88442 | 0.89085 | 0.88841 | 0.89323 | 0.90441 | 0.91453 | 0.9547 | 0.96978 | 1.0133 | 1.0278 | 1.0294 | 1.122 | 1.2297 | 1.2694 | 1.2834 | 1.3287 | 1.3301 | 1.3345 | N/A
Electricity | 23.0095 | 23.7341 | 24.3846 | 24.3188 | 24.2979 | 24.0224 | 23.662 | 23.0931 | 22.8024 | 22.6634 | 22.5459 | 22.5456 | 22.6888 | 22.9481 | 23.136 | 23.09 | 23.1542 | 23.2136 | 23.2305 | 23.3047 | 23.4291 | 23.4709 | 23.4338 | 23.4297 | 23.4804 | 23.589 | 23.596 | -0.02333%
Non-Renewable Energy Expenditures by Sector
(billion 2005 dollars)
Residential | 195.9888 | 215.1337 | 218.8056 | 221.2987 | 223.5004 | 221.1046 | 220.4384 | 218.0848 | 218.457 | 217.8497 | 219.4017 | 221.0029 | 224.5924 | 228.5306 | 230.9715 | 232.5716 | 236.0346 | 237.5802 | 240.4363 | 243.3919 | 247.2443 | 248.9877 | 251.0255 | 253.7327 | 257.2892 | 259.9643 | 262.2132 | 0.7947%
Commercial | 141.7785 | 154.3845 | 157.85 | 156.0653 | 159.3121 | 158.5368 | 157.9668 | 156.3502 | 157.3139 | 158.5888 | 160.742 | 163.3749 | 167.2082 | 172.0441 | 175.5826 | 178.0935 | 181.7399 | 185.0134 | 188.7905 | 192.8695 | 197.3603 | 201.1068 | 204.4923 | 208.5022 | 213.246 | 217.9738 | 222.082 | 1.465%
Industrial | 184.2294 | 196.0731 | 205.3986 | 217.8761 | 214.1478 | 207.1137 | 200.4842 | 191.8148 | 187.2922 | 184.9158 | 184.252 | 184.1145 | 186.8069 | 189.6626 | 190.4999 | 192.0311 | 194.883 | 196.8721 | 200.0719 | 202.1328 | 205.4881 | 206.9782 | 209.3091 | 212.8965 | 216.302 | 219.2678 | 222.0792 | 0.4994%
Transportation | 385.0011 | 474.6628 | 545.7236 | 538.7921 | 508.1102 | 488.4478 | 476.3778 | 463.414 | 458.1605 | 458.5728 | 452.7853 | 459.4185 | 469.7439 | 478.6719 | 487.8708 | 505.2935 | 511.0749 | 521.6462 | 538.7753 | 540.6428 | 554.2117 | 570.28 | 574.3004 | 588.9752 | 607.1214 | 615.455 | 632.7899 | 1.157%
Total Non-Renewable Expenditures | 906.9978 | 1040.2542 | 1127.7777 | 1134.0322 | 1105.0706 | 1075.2029 | 1055.2672 | 1029.6638 | 1021.2236 | 1019.9271 | 1017.181 | 1027.9108 | 1048.3514 | 1068.9092 | 1084.9248 | 1107.9896 | 1123.7323 | 1141.1119 | 1168.0741 | 1179.037 | 1204.3044 | 1227.3528 | 1239.1272 | 1264.1066 | 1293.9586 | 1312.6609 | 1339.1643 | 1.015%
Transportation Renewable Expenditures | 0.022793 | 0.033822 | 0.046833 | 0.042311 | 0.04638 | 0.050339 | 0.063797 | 0.071354 | 0.075695 | 0.080607 | 0.08248 | 0.089032 | 0.096232 | 0.10345 | 0.11268 | 0.13151 | 0.15409 | 0.1866 | 0.21708 | 0.24334 | 0.28576 | 0.31987 | 0.34809 | 0.38685 | 0.44324 | 0.46924 | 0.51464 | 11.5%
Total Expenditures | 907.0206 | 1040.288 | 1127.8246 | 1134.0746 | 1105.1169 | 1075.2532 | 1055.3311 | 1029.7352 | 1021.2993 | 1020.0077 | 1017.2635 | 1027.9998 | 1048.4476 | 1069.0126 | 1085.0375 | 1108.1211 | 1123.8864 | 1141.2986 | 1168.2911 | 1179.2803 | 1204.5902 | 1227.6726 | 1239.4753 | 1264.4934 | 1294.4019 | 1313.1301 | 1339.679 | 1.017%
1/ Includes energy for combined heat and power plants, except those whose primary business is to sell electricity, or electricity and heat, to the public.
2/ Excludes use for lease and plant fuel.
3/ Includes Federal and State taxes while excluding county and local taxes.
4/ E85 refers to a blend of 85 percent ethanol (renewable) and 15 percent motor gasoline (nonrenewable). To address cold starting issues, the percentage of ethanol actually
varies seasonally. The annual average ethanol content of 74 percent is used for this forecast.
5/ Sales weighted-average price for all grades. Includes Federal, State, and local taxes.
6/ Kerosene-type jet fuel. Includes Federal and State taxes while excluding county and local taxes.
7/ Diesel fuel for on-road use. Includes Federal and State taxes while excluding county and local taxes.
8/ Compressed natural gas used as a vehicle fuel. Includes estimated motor vehicle fuel taxes and estimated dispensing costs or charges.
9/ Includes electricity-only and combined heat and power plants whose primary business is to sell electricity, or electricity and heat, to the public.
10/ Weighted averages of end-use fuel prices are derived from the prices shown in each sector and the corresponding sectoral consumption.
Btu = British thermal unit.
N/A = Not applicable.
Note: Data for 2004 and 2005 are model results and may differ slightly from official EIA data reports.
Sources: 2004 and 2005 prices for motor gasoline, distillate fuel oil, and jet fuel are based on prices in the Energy Information Administration (EIA), Petroleum Marketing Annual 2005,
DOE/EIA-0487(2005) (Washington, DC, August 2006). 2004 residential and commercial natural gas delivered prices: EIA, Natural Gas Annual 2004, DOE/EIA-0131(2004)
(Washington, DC, December 2005). 2005 residential and commercial natural gas delivered prices: EIA, Natural Gas Monthly, DOE/EIA-0130(2006/04) (Washington, DC, April 2006).
2004 and 2005 industrial natural gas delivered prices are estimated based on: EIA, Manufacturing Energy Consumption Survey 1994 and industrial and wellhead prices from the
Natural Gas Annual 2004, DOE/EIA-0131(2004) (Washington, DC, December 2005) and the Natural Gas Monthly, DOE/EIA-0130(2006/04) (Washington, DC, April 2006). 2004
transportation sector natural gas delivered prices are based on: EIA, Natural Gas Annual 2004, DOE/EIA-0131(2004) (Washington, DC, December 2005) and estimated state taxes,
federal taxes, and dispensing costs or charges. 2005 transportation sector natural gas delivered prices are model results. 2004 and 2005 electric power sector natural gas prices:
EIA, Electric Power Monthly, May 2005 through April 2006, Table 4.11.A. 2004 and 2005 coal prices based on: EIA, Quarterly Coal Report, October-December 2005, DOE/EIA-0121
(2005/4Q) (Washington, DC, March 2006) and EIA, AEO2007 National Energy Modeling System run aeo2007.d112106a. 2004 and 2005 electricity prices: EIA, Annual Energy Review
2005, DOE/EIA-0384(2005) (Washington, DC, July 2006). 2004 and 2005 ethanol prices derived from weekly spot prices in the Oxy Fuel News. Projections: EIA, AEO2007 National
Energy Modeling System run aeo2007.d112106a.